## Page 1
PACT180D
PACKAGED AIR-COOLED 20 HP DUAL CIRCUIT SCROLL WITH TANK
DIMENSIONAL DRAWINGS
| LENGTH | WIDTH |  | HEIGHT |  | WEIGHT |  | TANK CAPACITY |  | FLUID CONNECTIONS
| 85" | 40" |  | 73" |  | 2100 LBS |  | 135 GAL. |  | 1 1/2" FPT
PRODUCT PERFORMANCE INFORMATION
REFRIGERANT | COMPRESSOR OPER. SUCTION TEMP. RANGE |  | LFT °F | 80°F AMB |  | 90°F AMB |  | 95°F AMB |  | 100°F AMB |  | 105°F AMB
|  |  |  | TONS | EER | TONS | EER | TONS | EER | TONS | EER | TONS | EER
R407C | 25°F to 55°F |  | 40 | 14.9632 | 10.57 | 14.0728 | 9.04 | 13.6427 | 8.34 | 13.1273 | 7.62 | 12.7108 | 7.02
|  |  | 50 | 18.4513 | 12.355 | 17.4112 | 10.63 | 16.929 | 9.86 | 16.4183 | 9.13 | 15.8861 | 8.42
|  |  | 60 | 22.3531 | 14.215 | 21.138 | 12.285 | 20.5791 | 11.42 | 20.0223 | 10.61 | 19.352 | 9.78
|  |  | 70 | 26.5997 | 16.06 | 25.1783 | 13.9 | 24.5415 | 12.96 | 23.8982 | 12.06 | 23.1522 | 11.18
R404A | -10°F to 45°F |  | 5 | 8.5137 | 6.09 | 7.6682 | 4.97 | 7.2463 | 4.47 | 6.7883 | 3.97 | 6.373 | 3.54
|  |  | 15 | 10.5618 | 7.21 | 9.5743 | 5.95 | 9.0802 | 5.38 | 8.5863 | 4.85 | 8.0918 | 4.36
|  |  | 30 | 14.1937 | 9.02 | 12.9241 | 7.525 | 12.2888 | 6.85 | 11.6532 | 6.21 | 10.9788 | 5.575
|  |  | 45 | 18.1618 | 10.76 | 16.6023 | 9.08 | 15.8062 | 8.3 | 15.0095 | 7.56 | 14.2123 | 6.86
|  |  | 60 | 22.381 | 12.34 | 20.4528 | 10.47 | 19.4965 | 9.61 | 18.556 | 8.81 | 17.5827 | 8.03
DRAKE REFRIGERATION INC
2900 SAMUEL DRIVE
BENSALEM, PA 19020
(888) 289-7299
www.drakechillers.com | [7 empty] | *ALL INFORMATION FOR REFERENCE ONLY

## Page 2
PACT180D
PACKAGED AIR-COOLED 20 HP DUAL CIRCUIT SCROLL WITH TANK
STANDARD FEATURES
FEATURE |  |  |  |  | BENEFIT
Listings |  |  |  |  | ETL 3046941, UL STD 1995, CAN/CSA STD, C22.2 No. 236
Microprocessor Control |  |  |  |  | Stand alone, simple, accurate control with over 10 years of field testing
Stainless Steel Brazed Plate Evaporator |  |  |  |  | Corrosion resistant evaporator wrapped in closed cell insulation
Copeland Scroll Compressor |  |  |  |  | Industry leader, long lasting compressor
Compressor Crankcase Heater |  |  |  |  | Prevents compressor damage caused by cold refrigerant on startup
Suction Accumulator |  |  |  |  | Protects the compressor from damage caused by liquid flood back by preventing liquid from entering the compressor
Water Flow Switch |  |  |  |  | Protects against process fluid freezing caused by fluid pump failure
Hot Gas Bypass |  |  |  |  | Aids in the prevention of evaporator freeze ups and capacity control
Copper Tube/Aluminum Fin Condenser |  |  |  |  | Rust resistant and high CFM
Painted Galvanized Steel Metal Cabinet |  |  |  |  | Sturdy, corrosion resistance, professional appearance
Insulated Process Fluid Lines |  |  |  |  | Maximum thermal efficiency
Factory Tested |  |  |  |  | Ensures the unit meets the customer's performance designed criteria and arrives in working order
Full Refrigerant Charge |  |  |  |  | Hassle free and more efficient installation
Stainless Steel Storage Tank |  |  |  |  | Closed cell insulation for increase temperature control with reliable, corrosion resistant, stainless steel recirculation pump
NEMA 3R Rated Electrical |  |  |  |  | Indoor/outdoor use
AVAILABLE OPTIONS
OPTIONS |  |  |  |  | AVAILABLE
Controls |  |  |  |  | BMS, BAS communications, remote access, monitoring services
Extended Warranty |  |  |  |  | 4 year extended compressor warranty
Electrical |  |  |  |  | Compressor fusing, phase monitors, disconnects and more
Stainless Steel Pumps |  |  |  |  | 1/3 HP to 25 HP on board pumps in multiple configurations & options
Fluid Piping Upgrades |  |  |  |  | Flow meters, pressure gauges, low flow bypass valves, and more
Coastal Protection/Hazardous Environments |  |  |  |  | Heresite coating, "Gold" and Copper condenser coils
Low Ambient Protection |  |  |  |  | Head pressure control for low ambient temperatures down to -20°F
Other |  |  |  |  | Tank sight glass, city water recovery, low liquid level alerts, etc.
More options and customization available, contact factory for information: (888) 289 - 7299
AVAILABLE MODEL NUMBER VOLTAGE REFERENCE
T3 (208-230/3/60) --- T4 (460/3/60) --- T5 (575/3/60)
PRODUCT INFORMATION
MODELS AVAILABLE |  | COMPRESSOR |  |  | FAN MOTOR |  | RLA EA | LRA EA | MCA | MOP | EVAP. PUMP EA
R407C | R404A | MODEL | QTY | HP | QTY | FLA EA
PACT180D3-T3-Z |  | ZB76KCE | 2 | 10 EA | 2 | 3.3 | 41.4 | 239 | 110 | 145 | 5.6
PACT180D3-T4-Z | [5 empty] | 1.6 | 19.2 | 125 | 50 | 65 | 2.8
PACT180D3-T5-Z | [5 empty] | 1.72 | 13.8 | 80 | 40 | 50 | 1.8
PACT180D6-T3-Z |  | ZB76KCE | 2 | 10 EA | 2 | 3.3 | 41.4 | 239 | 110 | 145 | 5.6
PACT180D6-T4-Z | [5 empty] | 1.6 | 20 | 125 | 55 | 70 | 2.8
PACT180D6-T5-Z | [5 empty] | 1.72 | 13.2 | 80 | 35 | 45 | 1.8
DRAKE REFRIGERATION INC
2900 SAMUEL DRIVE
BENSALEM, PA 19020
(888) 289-7299
www.drakechillers.com | [6 empty] | *ALL INFORMATION FOR REFERENCE ONLY